# Hydroponics Monitoring & Automation System

Engineering Design, Integration & Troubleshooting Dossier

## Project Overview

Objective: Develop an embedded hydroponics monitoring and automation platform using a Raspberry Pi Compute Module 4 (reTerminal) and Grove Base HAT. This document records verified hardware, software, troubleshooting, current status, and remaining work. Only verified information is included.

## Hardware Configuration

Main Controller:
- Raspberry Pi Compute Module 4 (BCM2711, 4 GB RAM)
- Raspberry Pi OS Bookworm

Expansion Board:
- Seeed Studio Grove Base HAT V1.0

Sensors:
- DFRobot Gravity Analog pH Sensor (Grove A2)
- DFRobot EC Sensor (analog, channel not verified)
- Waveshare DHT22 (Grove D5)
- Waterproof DS18B20 via Grove D16

Other Hardware:
- Two motor drivers connected (not tested).

## Software Environment

Python 3.13

Verified packages:
- adafruit-blinka
- adafruit-circuitpython-dht
- grove.py
- smbus2
- w1thermsensor

Backend includes Flask, Socket.IO, OpenCV, NumPy, GPIO libraries, ReportLab and ManualADC implementation.

## Verified Components

Verified Working:
- Raspberry Pi CM4
- Grove Base HAT
- I²C communication
- ManualADC interface (0x04)
- DHT22 sensor
- pH analog output

Not Yet Tested:
- EC sensor
- Motor drivers

Suspected Faulty:
- Waterproof DS18B20 temperature sensor

## Troubleshooting Summary

DS18B20:
- w1_therm module loaded successfully.
- Overlay updated to dtoverlay=w1-gpio,gpiopin=16.
- Linux detected invalid family code (00-xxxxxxxxxxxx).
- ESP8266 testing also failed (-127°C / No device found).
- Previous overheating reported.
Conclusion: sensor is the primary suspected hardware failure.

DHT22:
- Successful repeated readings (30–32°C, 65–77% RH).
- Occasional checksum warnings did not prevent normal operation.

pH:
- Analog readings varied dynamically from approximately 206 to 2115.
- Communication verified.
- Calibration intentionally deferred.

## Remaining Tasks

1. Test EC sensor.
2. Calibrate pH sensor using laboratory pH meter.
3. Replace or verify DS18B20 sensor.
4. Test motor drivers.
5. Integrate verified sensors into hydroponics application.

## Current Project Status

The embedded platform, Grove Base HAT, digital interface, analog interface, DHT22 sensor, and pH sensor communication have all been validated. The only consistently failing component across Raspberry Pi and ESP8266 testing is the waterproof DS18B20 sensor. Calibration and integration work remain pending.